ENVIRONMENTAL JUSTICE FORUM (EJF), Hyderabad                                                      under LEAD Foundation

Date: 10th May 2026

To
Dr G. Sabita Reddy,
Chairperson,                                                                                                      State Level Environment Impact Assessment Authority (SEIAA), Telangana

Sub: Serious Scientific, Regulatory, and Environmental Justice Failures in the Environmental Appraisal and Environmental Clearance of Hyperscale Data Centres in Telangana - Uphold the Precautionary Principle etc.- Request - Reg.

Ref: 1. Proposal No.SIA/TG/MIS/136947/2020; EC No.SEIAA/TS/OL/RRD-468/ 2019-4 dt.Feb.8, 2020 for Data Centre at Meerkhanpet by ADS.

2. Proposal No.SIA/TG/MIS/173950/2020; EC for Data Centre@Raviryal by ADS.

3. Proposal No.SIA/TG/MIS/137046/2020; EC No.SEIAA/TS/OL/RRD-467/ 2019-375 dt.Feb.8, 2020 for the Data Centre @Chandanvelly by ADS.

4. Proposal No.SIA/TG/MIS/137046/2020; EC No.SEIAA/TS/OL/RRD-467/ 2019-375 dt.Feb.8, 2020 for Data Centre @Peddavedu by ADS.

5. Proposal No.SIA/TG/MIS/119360/2019 @Manchanpally by CtrlS.

6. EIA Notification 2006 as amended up to date.

Respected Madam,

We, from Environmental Justice Forum, Hyderabad, respectfully submit this representation highlighting the major scientific, procedural, and environmental governance deficiencies in the appraisal and grant of Environmental Clearances to hyperscale data centre projects proposed by Amazon Data Services and CtrlS in Telangana.

The EIA/EMP documents show that these projects were appraised under the generic category of “Building and Construction Projects” [Item 8(a)], without even basic disclosures on grid and non-grid power requirements.

However, hyperscale data centres are industrial-scale energy and thermal infrastructures with environmental footprints far exceeding ordinary commercial buildings due to their massive 24×7 electricity demand, intensive cooling systems, backup power infrastructure, hazardous-material handling, and associated heat and emissions impacts.

The present appraisal framework fails to adequately assess these critical operational and environmental aspects, thereby compromising the scientific and procedural integrity of the environmental clearance process, as detailed below:

1. Lack of Transparency in sharing information on basic energy demands The EIA/EMP documents reveal that these projects were appraised under the generic Category B2 “Building and Construction Projects” under 8(a) of Schedule I of EIA Notification 2006 which are exempted from public hearing, without even basic information like the source and quantum of grid electricity supply for each data centre from non-renewable and renewable sources (and the captive power capacity proposed by each, if any), and its adverse impact on the regional electricity grid.

The inappropriate categorisation of hyperscale data centres as ordinary building projects and inadequate transparency and scientific disclosure undermines environmental governance, environmental justice, and the Right to Life under Article 21 of the Constitution.

2. Failure to Assess Cooling Systems and Thermal Management
The most serious omission in the EIA/EMP documents is the near-total absence of technical disclosure regarding cooling systems, which constitute the central operational and environmental component of any hyperscale data centre.

The documents fail to disclose or evaluate:
• Type of cooling technology proposed, to minimize the energy demand                                   • Cooling-water / air demand and consumption patterns;                                                           • Thermal load calculations and cooling-energy demand;
• Heat rejection quantities and thermal dispersion pathways;
• Cooling-system blowdown characteristics;
• Refrigerant inventories and leakage risks.

Without such disclosures, meaningful assessment of water demand, thermal pollution, energy efficiency, greenhouse gas emissions, and long-term environmental risks becomes impossible.

3. Scientific Implausibility in the Peddavedu Project Appraisal
Reported Characteristics:
• Power Demand: 278 MW
• DG Sets: 110 × 3500 kVA
• Total Water Demand: 302.1 KLD
• Virtually no allocation for cooling operations

Hence, the above representation is scientifically implausible.

A facility operating at nearly 278 MW would generate enormous continuous heat loads requiring substantial cooling infrastructure. Such thermal loads cannot realistically be managed with negligible cooling-water demand unless critical cooling-related operational details are omitted.

4. Omission of Thermal Pollution and Microclimatic Impacts
The EMPs contain no assessment of:
• Urban Heat Island amplification;
• Thermal plume dispersion;
• Impacts on local temperatures;
• Effects on nearby ecology, agriculture, and habitations;
• Regional climate implications.

The complete absence of thermal impact modelling represents a major scientific lacuna.

5. Inadequate Assessment of DG Emissions and Air Quality Impacts
The projects involve industrial-scale backup power systems comparable to heavy industrial installations.

The appraisal ignores:
• Simultaneous DG operations during grid failures;
• Long-duration emergency operation scenarios;
• Cumulative regional air-quality impacts;
• Health impacts on nearby communities.

This approach is inconsistent with accepted environmental risk assessment principles.

6. Overlooked Industrial Hazards
The EMPs inadequately assess:
• Lithium-ion battery risks;
• Thermal runaway and toxic smoke;
• Firewater contamination;
• Refrigerant leakage;
• PFAS-related groundwater contamination risks.

Given the persistence and toxicity of PFAS compounds, the absence of disclosure and risk assessment is a matter of grave concern.

7. Environmental Justice and Procedural Deficiencies
Key deficiencies include:
• Outdated groundwater assessments based on 2011–12 data;
• No cumulative impact assessment;
• Inadequate public transparency regarding operational and environmental risks.

Such omissions undermine the principles of informed decision-making, public participation, and environmental justice embedded in environmental governance jurisprudence.

Requested Corrective Actions

1. Reclassify and re-examine: the hyperscale data centres as industrial infrastructure projects rather than under Item 8(a) Building and Construction projects, make the information on their capacity and electricity demands, and their impacts on regional power grid public, and reevaluate the granted ECs.

2. Mandate: technical disclosures by the project proponents to submit supplementary reports on:
• Thermal load calculations, Cooling technology specifications, Cooling-water balance, and Waste heat management plans;
• Power Usage Effectiveness (PUE);
• Annual GHG inventories;
• Refrigerant and PFAS disclosures.

3. Conduct: an independent cumulative impact study for the Ranga Reddy corridor covering:
• Water demand; Electricity consumption; Heat emissions; Air quality impacts;
and Climate resilience.

4. Develop: sector specific environmental appraisal guidelines for hyperscale data centre projects.
The rapid expansion of digital infrastructure must not compromise ecological sustainability, groundwater security, public health, or environmental justice.

Finally, we trust that the Authority will uphold the Precautionary Principle, sustainable development, and intergenerational equity through a scientifically rigorous, transparent, and accountable environmental appraisal process that protects both people and the environment.

Annexure: Summary of Key Scientific Omissions (for quick reference)

Yours sincerely,

Signatories (on behalf of Environmental Justice Forum (EJF) under LEAD Foundation, Hyderabad)

- Dr P. Narayana Rao, Editor, Environment & People
Former Member, APPCB, Convener, EJF.

- Er G. Kondala Rao, CE (Public Health) Rtd., Co-Convener, EJF.

- Sri Prasad Jaladi, Founder, suraksha.org

- Ms Nirmala Sambamoorthy,  Management Consultant, EC Member, EJF.

- Er Suryadevara Ravi, Former Sr Scientist, DAE, Govt. of India; suryadevara.ravi@gmail.com

- Ms Anuradha, Policy and Practice Forum

- Er P. Narasimha Rao, FIE, Past Chairman, ECM, IEI TSC.

- Prof G. Suresh Babu, Dept. of EEE, CBIT, Hyderabad.

- Er Dilip Bhattalwar, Ex. GM, SAIL, Certified Energy Auditor. dilipbhattalwar@gmail.com

- Er Venkat Katta, Director-Technology, venkatkatta@atpole.com

- Dr A.V. Rao, Consultant, Certified Energy Auditor. Member, ECM, IEI TSC, Visiting Professor, UPES & JNTUK.

- Sri Sundeep Kottakki, Green Earth, Water, Air.

- Sri Ashok Kumar Ageer, Green Earth, Water, Air.

- Er Manas D. Rath, Policy and Practice Forum.

Copy to:
• Members, SEAC Telangana
• Member Secretary, TSPCB

Annexure: Summary of Key Scientific Omissions (for quick reference)

| Environmental Parameter | Reported in EMP | Scientifically Required Assessment |
| --- | --- | --- |
| Cooling Water Demand | Near-zero | Full cooling-water balance, thermal management analysis |
| Emissions | No major point-source emissions | Assessment of emissions from large DG infrastructure |
| Waste Heat | Not assessed | Continuous thermal-rejection and dispersion modelling |
| Hazardous Waste | Generic categorisation | Assessment of batteries, refrigerants, PFAS risks |
| Air Quality | Generic baseline analysis | Simultaneous DG operation, cumulative regional modelling |
| Climate Impact | Not assessed | GHG inventory and energy-efficiency evaluation |
| Cumulative Impacts | Not assessed | Regional carrying-capacity assessment |